Point allocation based on key parameters

| Metric | Category | Proposed Weight (Max Points) | Rationale |
| --- | --- | --- | --- |
| Overload | Power demand | 25 | High risk of rapid insulation degradation and catastrophic failure. |
| Power Cuts/Outages | Power supply | 25 | Direct impact on reliability and end-user downtime. |
| Current Unbalance | Power quality | 15 | Causes localized heating and reduces transformer capacity. |
| Neutral Current | Power quality | 15 | Severe risk of neutral conductor overheating and tank heating. |
| Power Factor | Power demand - use of reactive power ; so it’s the consumer who drives the pf level, not the utility | 10 | Primarily an efficiency/utility penalty issue, though it increases line current. |
| High THD | Power quality | 10 | Causes chronic eddy current losses, but less of an acute fire/failure risk than neutral overloads. |
| Total |  | 100 Points |  |

How points are allocated

| Parameter | Max Points | Normal (Full Points) | Warning (Sliding Scale) | Critical (0 Points) | Special Conditions |
| --- | --- | --- | --- | --- | --- |
| 1. Overload | 25 | ≤ 95% load | Drops linearly from 25 down to 0 points as load increases from 95% to 120%. | > 120% load | Underloaded cases (< 30% load) are automatically assigned 15 points since they offer a free pass to some other issues. |
| 2. Power Cuts / Outages | 25 | 0 minutes | Two-Stage Drop: • 0-60 mins: Drops from 25 to 10 • 60-240 mins: Drops from 10 to 0 | > 240 minutes | Evaluated over a month. |
| 3. Neutral Current | 15 | ≤ 30% of average current | Drops linearly from 15 down to 0 points as neutral current increases from 30% to 50%. | > 50% of average current | Free Pass: Automatically gets 15 points if Load Rate < 30%. |
| 4. Current Unbalance | 15 | ≤ 40% | Drops linearly from 15 down to 0 points as unbalance increases from 40% to 70%. | > 70% | Free Pass: Automatically gets 15 points if Load Rate < 30%. |
| 5. Power Factor | 10 | ≥ 0.8 | None. (This metric operates on a strict pass/fail basis). | < 0.8 | Free Pass: Automatically gets 10 points if Load Rate < 30%. |
| 6. High THD | 10 | ≤ 5% | Drops linearly from 10 down to 0 points as THD increases from 5% to 8%. | > 8% | Free Pass: Automatically gets 10 points if Load Rate < 30%. |

Grading based on cumulative points

| Grade | Point Range | Status | Implications |
| --- | --- | --- | --- |
| A | 90 - 100 | Healthy | Operating normally. It might have a minor inefficiency (like a poor Power Factor losing 10 points, or a brief 15-minute outage). |
| B | 75 - 89 | Monitor | The site has hit at least one major warning threshold (e.g., a 1-hour outage drops 15 points, or critical neutral current drops 15 points). |
| C | 60 - 74 | At Risk | The site has hit a major critical threshold (e.g., >120% Overload loses 25 points) OR is suffering from multiple compounding warnings (e.g., high THD + unbalance). |
| D | < 60 | Critical | The site is experiencing multiple critical failures simultaneously (e.g., >120% Overload AND >50% Neutral Current). Risk of catastrophic failure. |

Sample scoring for sites in January 2026